POTABLE WATER STORAGE TANK SPECIFICATION POWDER COATED BOLTED STEEL TANK

# PART 1 – GENERAL

  - SCOPE OF WORK

    - Furnish and erect bolted RFP (rolled, flat panel) steel tank for storage. Scope to include tank structure, factory Thermoset Epoxy Powder Coat process and tank appurtenances as shown on the contract drawings and described herein.

    - All required labor, materials and equipment shall be included.

  - QUALIFICATIONS OF TANK SUPPLIER

    - The Engineer’s selection of factory applied Thermoset Epoxy Powder coated bolted steel tank is predicated on a thorough examination of design criteria, construction methods, and optimum coating for resistance to internal and external tank corrosion. Deviations from the specified design, construction or coating details will not be permitted.

    - The bidder shall offer a new tank structure as supplied from a manufacturer specializing in the design, fabrication and erection of factory applied Thermoset Epoxy Powder coated, bolt together tank systems. The manufacturer shall own and operate its steel fabrication and coating facilities.

    - The tank installation as shown on the plans and specified herein, is based on the equipment furnished by one supplier. A tank which is offered as a substitute to the specific requirements of these Specifications and which differs in detail and arrangement from that shown may require changes in design and construction. All costs which result from such changes in design and construction are to be borne entirely and unconditionally by the Supplier; said costs to include but not be limited to structural, piping, mechanical and electrical changes and all engineering costs incurred as a result of the substitution, in the revision of Plans and Specifications, review of design changes by others, preparation of change orders, and any other costs directly resulting from said substitution.

    - The tank shown on the contract drawings and specified herein will be a Super Durable Polyester Powder coated, RFP bolted tank as manufactured by Tarsco Bolted Tank, Inc. of Goodman, Missouri.

    - Strict adherence to the standards of design, fabrication, erection, product, quality, and long-term performance, established in this Specification will be required by the Owner and Engineer.

    - Tank suppliers wishing to pre-qualify shall submit the following to the Engineer/Owner for consideration:

      - Typical structure drawing(s)

      - List of tank materials, appurtenances, and tank coating technical specifications.

      - Resume of job installation superintendent.

      - The erector shall be certified by the manufacturer and an employee of the tank manufacturer experienced and with knowledge necessary to furnish and erect the highest quality tank possible. If the erector is not an employee of the tank manufacturer, then the tank manufacturer must supply an employee experienced in tank erection to be on site during the entire erection process.

      - If a dome roof system is required, the dome erector must have installed, and had in satisfactory service, for a period of not less than five years, at least one clear span aluminum dome with a diameter equal to or larger than the unit specified, and shall submit evidence of such with his bid proposal and/or pre-bid submittal.

      - The components of the tank that come in contact with stored water shall be certified to meet ANSI/NSF Additives Standard No. 61.

      - The Engineer reserves the right to evaluate all bids based on long term operation, coating, and maintenance costs. Values to be used in this evaluation will be at the discretion of the Engineer, as detailed in this specification and bid tabulation form. The Engineer will add such costs, dependent upon the type of tank offered, to the bidder’s price to determine the effective low bid for purposes of making the award.

  - SUBMITTAL DRAWINGS AND SPECIFICATIONS

    - Construction shall be governed by the Owner’s drawings and specifications showing general dimensions and construction details, after written approval by the Engineer of detailed erection drawings prepared by the tank bidder. There shall be no deviation from the drawings and specifications, except upon written order from the Engineer.

    - The bidder is required to furnish, for the approval of the Engineer and at no increase in contract price, __________sets of complete specifications and construction drawings for all work not shown in complete detail on the bidding drawings. A complete set of structural calculations shall be provided for the tank structure and foundation. Final approved drawings and calculations shall be stamped by a Licensed Professional Engineer or Structural Engineer licensed in the state in which the project is located.

    - When approved, two sets of such prints and submittal information will be returned to the bidder marked “APPROVED FOR CONSTRUCTION” and these drawings will then govern the work detailed thereon. The approval by the Engineer of the tank supplier’s drawings shall be an approval relating only to their general conformity with the bidding drawings and specifications and shall not guarantee detail dimensions and quantities, which remains the tank manufacturers responsibility.

# PART 2 – DESIGN CRITERIA

  - TANK SIZE

    - The Super Durable Polyester Powder coated bolt together tank shall have a nominal diameter of

________ft. with a nominal sidewall height (to roof eave) of ____________ft.

  - TANK CAPACITY

    - Tank capacity shall be __________ gallons (nominal)

    - Freeboard space in top of tank shall be ________ inches.

  - FLOOR ELEVATION

2.3.1 Finished floor elevation shall be set at elevation shown on the drawings or at _____________.

  - TANK DESIGN STANDARDS

2.4.1  The materials, design, fabrication, and erection of the bolt together tank shall conform to the AWWA

Standard for “Factory-Coated Bolted Steel Tanks for Water Storage” – ANSI/AWWA D103.

2.4.2  The tank coating system shall conform solely to Section 12.6 Thermoset Powder Coatings of

ANSI/AWWA D103.

2.4.3  All materials furnished by the tank manufacturer which are in contact with stored water shall be certified

to meet ANSI/NSF Additives Standard No. 61. Certification of a coating type alone will not be sufficient

to meet this requirement. Certification of a distributor, and not the tank or coating manufacturer, will not

be accepted.

2.4.4  American Institute of Steel Construction (AISC) “Steel Construction Manual”, 14th Edition.

  - DESIGN LOADS

2.5.1 Specific Gravity ________________

2.5.2	Design Freeboard ______________inches

2.5.3	Wind Velocity ________________mph

2.5.4	Roof Snow Load ______________psf.

2.5.5  Roof Live Load _______________psf.

2.5.6  Tank working capacity shall be ___________________ gallons (useable, U.S. Gallons)

2.5.7	Earthquake Seismic Use Group per AWWA D 103 (Use Group: I, II, or III) ________________

2.5.8	Seismic Site Class A, B, C, or D _______________

2.5.9  pH Level ranges from __________Min. to __________Max.

2.5.10 Operating temperature of the product is ____________ degrees F°.

# PART 3 – MATERIAL SPECIFICATIONS

  - PLATES AND SHEETS

    - Plates and sheets used in the construction of the tank shell, tank floor (when supplied) and tank roof, shall comply with the minimum standards of AWWA D103, Sec. 4.4.

    - Design requirements for mild strength steel shall be ASTM A1011 or ASTM A572, Grade 50 with a design strength as defined in AISC, unless otherwise noted in the engineering specifications and/or submittals.

    - Design requirements for high strength steel shall be ASTM A1011 or ASTM A572, Grade 60, 70 and/or 80 with a design strength as defined in AISC, unless otherwise noted in the engineering specifications and/or submittals.

  - ROLLED STRUCTUAL SHAPES

    - Carbon Material shall conform to minimum standards of ASTM A36 or ASTM A992.

  - HORIZONTAL WIND STIFFENERS

    - Intermediate horizontal wind stiffeners may be of the web truss or rolled angle design to create multiple layers of stiffener, or structural members permitting wind loads to distribute around tank.

  - BOLT FASTENERS

    - Predominate Bolts used in tank lap joints are ½ - 13 UNC-2A rolled thread, per SAE J429, Gr. 8.2. Larger tanks may include 5/8” or ¾” diameter bolts also meeting the requirements of SAE J429, Gr. 8.2.

    - Bolt Material

      - SAE J429-Grade 8/ASTM F3125 (1/2” Fin-Neck Tank bolts)

        - Tensile Strength – 150,000 psi Min.

        - Proof Load – 120,000 psi Min.

      - The grades of all other hardware to be as listed on contract drawings.

    - Bolt Finish – Zinc, mechanically deposited the meet NSF 61 Approval.

    - Bolt Head Encapsulation

      - High impact polypropylene copolymer encapsulation of entire bolt head up to the splines

on the shank’s used in any tanks containing a liquid.

      - Resin shall be stabilized with an ultraviolet light resistant material such that the color shall

appear black. The bolt head encapsulation shall be certified to meet the ANSI/NSF Standard 61

for indirect additives.

    - All bolts on the vertical tank wall shall be installed such that the head portion is located inside the tank, and the washer and nut are on the exterior.

    - Bolt lengths shall be sized to achieve a neat and uniform appearance with typically 0-4 threads extending beyond the nut after torqueing.

    - All lap joint bolts shall be properly selected such that threaded portions of the bolts will not be exposed to the “shear plane” between tank sheets greater than ¼” in thickness.

    - All lap joint bolts shall include a minimum of four (4) splines on the underside of the bolt head at the shank in order to resist rotation during torqueing.

  - SEALANTS

    - The lap joint sealant shall be a one component, moisture cured, polyurethane compound. The sealant shall be suitable for contact with potable water and shall be certified to meet ANSI/NSF Additives Standard 61 for indirect additives.

    - The sealant shall be used to seal lap joints and bolt connections and edge fillets for sheet notches and starter sheets. The sealant shall cure, have excellent adhesion to the Thermoset Epoxy Powder coating, low shrinkage, and be suitable for interior and exterior use.

    - Sealant curing time is typically is 24 hours minimum at 73°F and 50% RH

    - Tack-free time: 6 to 8 hours

    - Final cure time: 10 to 12 hours

# PART 4 – FACTORY POWDER COAT PROCESS

  - SURFACE PREPARATION

    - Sheets and tank components shall be blasted on both sides providing an SSPC SP10 (near white blast) surface profile.

    - The surface anchor pattern shall not be less than 1.0 Mils.

  - CLEANING

    - Following surface preparation, sheets and tank components shall be thoroughly washed, rinsed and coated

with Zirconium.

    - Washing shall be with a suitable detergent using such concentrations as recommended for removing shot

dust. Water temperature will be elevated to improve the effects of the cleaning process.

    - The soap concentration shall be monitored and maintained daily according to the range recommended for

use by the manufacturer for the cleaning process.

    - Rinsing shall be in a two-stage booth. A R.O water rinse shall be used in the first and second wash

system.

    - After rinse stage, the sheets and tank components will then move into the protective coating (Zirconium)

stage.

  - POWDER COATING

    - After cleaning and blasting, the sheets and tank components shall receive a Thermoset Epoxy powder coating on both sides of steel. The powder coating shall be applied with an electrostatic process. The thermoset powder coat system shall be as specified:

LIQUID STORAGE	POWDER COAT SYSTEM	DFT* Range	.

| Interior Lining | THERMOSET EPOXY | See Para. 4.4.2 |
| --- | --- | --- |
| Exterior Coating | SUPER DURABLE POLYESTER | See Para. 4.4.3 & 4.4.4 |

*DFT – Nominal dry film thickness

    - Interior Prime coating, Thermoset Epoxy will be applied at 8 mils nominal DFT, with a min/max range from 8-10 mils avg.

    - Exterior Prime coating, Thermoset Epoxy will be applied at 5 mils nominal DFT

    - Exterior coating, Super Durable Polyester will be applied at 3 mils nominal DFT, with a min/max range from 3-5 mil avg.

    - Coating thickness shall be maintained by the use of PLC controlled automatic spray guns preset for the application, along with applicable re-enforcement during the application process.

    - Visual inspection for coverage shall be made after powder application and before the first oven cure. Areas with light coverage shall be re-sprayed with a manual spray gun.

  - POWDER CURING GEL

    - Sheets and tank components shall then be heated in an oven to cause the powder to gel adequately to cross-link with topcoat.

    - Visual inspection and dry film test shall be randomly performed before application of topcoat.

  - SUPER DURABLE POLYESTER TOPCOAT

    - SDP topcoat shall be applied on all exterior surfaces at 3 mils nominal DFT, with a range from 3-5 mil avg.

    - The SDP topcoat shall provide excellent gloss retention and UV resistance. Color to be selected from standard colors (chart) with special formulated and premium colors as available options.

    - Visual inspection will be performed randomly before the curing oven.

  - FINAL CURING

    - Sheets and tank components shall then pass through the final cure oven. Oven temperature settings will be based on the proprietary data provided by the coating suppliers. Oven temperatures vary depending on metal thickness.

  - INSPECTION

    - During final cool down, sheets shall be randomly inspected for cure, adhesion, coating thickness and holidays.

    - Cure shall be controlled by comparing oven data and may be verified using random MEK rub tests.

    - X-Adhesion shall be confirmed (ASTM D3359-Method A).

    - Coating thickness shall be confirmed using dry film thickness gage (SSPC PA-2).

    - Holiday testing shall be performed with Low Voltage Wet Sponge Testing according to ASTM D5162, Method A (or equivalent).

    - Quarterly Data Pak’s shall be run through the paint line for compliance.

  - PACKAGING

    - After cooling down and inspection, the sheets and tank components shall be unloaded and packaged for shipment.

    - Sidewall sheets, Roof sheets and Floor sheets shall be stacked on wooden skids with foam or paper placed between each sheet to prevent any scuffing. Skids shall be loaded to 6,000-pound maximum weight. Each skid of sheets will be bolted down to the wooden skid and shall be wrapped in heavy mil, blue poly reinforced plastic.

# PART 5 – TANK STRUCTURE

  - THERMOSET EPOXY POWDER COATED STEEL FLOOR

    - The floor is to be a Thermoset Epoxy Powder coated bolted steel floor. Bolted steel panels shall be placed over a compacted granular base contained by a steel or concrete ring wall, or a concrete slab. A non-extruding and resilient bituminous type filler, meeting the requirements of ASTM D1751, should be placed between the tank floor and concrete ring wall or between the tank floor and concrete slab to act as a cushion.

    - A plastic encapsulated nut shall be used to cover the bolt threads exposed on the inside of the floor.

    - Leveling the starter ring shall be required and the maximum differential elevation within the ring shall not exceed one-fourth (1/4) inch, nor exceed one-eighth (1/8) inch within any thirty (30) feet of length.

OR

  - ALTERNATIVE EMBEDDED BASE SETTING RING AND CONCRETE FLOOR

    - The floor design is of reinforced concrete with an embedded Super Durable Polyester coated steel starter sheet per the manufacturer’s design and in accordance with AWWA D103, Sec. 13.4.6, Type 6.

    - A leveling assembly shall be used to secure the started ring, prior to encasement to concrete. Installation of the starter ring on concrete blocks or bricks, using shims for adjustment, is not permitted.

    - Leveling the starter ring shall be required and the maximum differential elevation within the ring shall not exceed one-fourth (1/4) inch, nor exceed one-eighth (1/8) inch within any thirty (30) feet of length.

    - Place one elastomer water stop seal strip on the inside surface of the starter ring below concrete floor line as noted on design drawings. Install materials in accordance with tank manufacturer’s instructions.

  - SIDEWALL STRUCTURE

    - Field erection of the Super Durable Polyester Powder coated bolted steel tank shall be in strict accordance with the procedures outlined by the manufacturer, using factory trained and qualified personnel.

    - Particular care shall be taken in handling and bolting of the tank panels and members to avoid abrasion of the coating system. Prior to a liquid test, the qualified personnel may visually inspect all surface areas.

    - Holiday (electrical leak rate) testing is performed at the factory in accordance with Sec. 4.7. Holiday Testing is not performed in the field unless specified by the owner. All defects of paint during erection are repaired in accordance with manufacturer’s published touch up procedures.

    - The placement of sealant on each panel may be owner inspected prior to placement of adjacent panels. However, the qualified personnel shall not relieve the bidder from his responsibility for liquid tightness.

    - No backfill shall be placed against the tank sidewall without prior written approval and design review of the tank manufacturer. Any backfill shall be placed according to the strict instructions of the tank manufacturer.

  - ROOF

    - Thermoset Epoxy Powder-coated steel deck.

      - Tank shall include a sectioned roof fabricated from Thermoset Epoxy Powder-coated, bolted steel panels, as produced by the tank manufacturer, and shall be assembled in a similar manner as the sidewall panels. The roof shall be clear-span and self-supporting or center supported. Both live and dead loads shall be carried by the tank walls and any center supports. The manufacturer shall furnish a roof opening which shall be placed near the outside tank ladder and which shall be provided with a hinged cover and a hasp for locking. The opening shall have a clear dimension of 24” x 24”. The opening shall have a curb at least 4” in height and the cover shall have a downward overlap of at least 2” , or a gasketed weather-tight cover in lieu of the four (4”) inch curb and two (2”) inch overlap. Per AWWA D103, Sec. 7.6.

OR

    - Alternative Clear-span Aluminum Dome

      - The roof shall be constructed of non-corrugated triangular aluminum panels, which are sealed and firmly clamped in an interlocking manner to a fully triangulated aluminum space truss system of wide flange extrusions, thus forming a dome structure.

      - The dome shall be clear span and designed to be self-supporting from the periphery structure with primary horizontal thrust contained by an integral tension ring. The dome dead weight shall not exceed 3 pounds per square foot of surface area.

      - The dome and tank shall be designed to act as an integral unit. The tank shall be designed to support an aluminum dome roof including all specified live loads.

5.4.2.4   Materials: Are designed per AWWA D103-2009 with 2014 Addendum.

  - APPURTENANCES

    - Pipe Connections

      - Where pipe connections are shown to pass through tank panels, they shall be factory located, saw cut, (acetylene torch cutting or welding is not permitted), and utilize an interior and exterior flange assembly and the tank shell reinforcing shall comply with AWWA D103, Sec. 7.2. A single component urethane sealer shall be applied on any cut panel edges or bolt connections.

      - Overflow piping shall be ________ inches nominal diameter schedule 10 carbon steel coated externally or schedule 40 PVC. A 90-degree internal weir elbow with external down comer pipe and flap valve shall be provided for the overflow.

      - Inlet and outlet connections shall conform to the sizes and locations specified on the plan sheets.

    - Outside Tank Ladder

      - An outside tank ladder shall be furnished and installed as shown on the contract drawings. Per AWWA D103, Sec. 7.4.1

      - Ladders shall be fabricated of steel and utilize skid-resistant rungs. Finish shall be hot dipped galvanized or coated Safety Yellow.

      - If required, Safety Cage and Step-Off Platforms are required these shall be factory coated or painted Safety Yellow as listed on engineering drawings. Ladders will be equipped with a hinged lockable entry device and comply with OSHA 1910.28 (b) (9). Finish shall be factory coated unless specifically defined by the buyer.

    - Access Doors

      - One manway shall be provided as shown on the contract drawings in accordance with AWWA D103, Sec. 7.1.2.

      - The manhole opening shall be _________ inches in diameter. The access door (shell manhole) and the tank shell reinforcing shall comply with AWWA D103, Sec. 7.1.2

    - Roof Vent

      - A properly sized vent assembly in accordance with AWWA D103, Sec. 7.7 shall be furnished and installed above the maximum water level so that at maximum design rate of water fill or withdrawal.

      - The overflow pipe shall not be considered to be a tank vent.

      - The vent shall be so designed in construction as to prevent the entrance of birds and/or animals by including an expanded aluminum screen (1/2 inch) opening.

    - Roof Hatch

      - The manufacturer shall furnish a roof opening which shall be placed near the outside tank ladder and which shall be provided with a hinged cover and a hasp for locking. The opening shall have a clear dimension of at least twenty-four (24” x 24”) square. The opening shall have a curb, at least four (4) inches in height and the cover shall have a downward overlap of at least two (2) inches.

    - Roof Perimeter or Partial Guardrail

      - Perimeter or Partial guardrail and toe board of the deck shall be provided and installed as specified on the project drawings.

    - Liquid Level Indicator

      - A liquid level indicator with stainless steel float, number board, and high visibility target shall be provided and installed as detailed on the project drawings.

    - Sensors

      - High and low water level sensors are to be provided to monitor the high and low water levels in

the tank as shown on the plan sheet.

    - Identification Plate

      - A manufacturer’s nameplate shall list the tank serial number, tank diameter and height, and maximum design capacity. The nameplate shall be affixed to the tank exterior sidewall location approximately five (5) feet from the grade elevation in a position of unobstructed view.

# PART 6 – INSTALLATION

  - INSTALLATION PROCESS

    - Field erection of the bolted steel tank will be in strict accordance with manufacturer’s procedures using factory trained and certified erectors.

    - Particular care will be taken to protect the baked-on powder coated panels from damage (i.e., scratches, abrasion) during field installation.

    - Tank to be constructed utilizing synchronized hydraulic jack process, which keeps construction crews at grade level for safety and point access quality control.

    - Any coating damage will be repaired per manufacturer’s recommendations.

    - No backfill shall be placed against the tank sidewall during or after the construction process.

  - FIELD TESTING

    - Hydrostatic

      - Following completion of erecting and cleaning of the tank, the structure shall be tested for liquid tightness by filling tank to its overflow elevation.

      - The contractor in accordance with the manufacturer’s recommendations shall correct any leaks disclosed by this test.

      - The owner shall furnish water required for testing at the time of tank erection completion and at no charge to the tank erector. Disposal of test water shall be the responsibility of  the owner.

PART 7 – DISINFECTION

7.1      Standards

7.1.1 The tank structure shall be disinfected at the time of testing by chlorination in accordance with

AWWA Standard C652 “Disinfection of Water Storage Facilities” as modified by the tank

manufacturer.

7.1.2	Disinfection shall not take place until tank sealant is fully cured (see Sec. 3.5.5).

7.1.3	Acceptable forms of chlorine for disinfection shall be:

7.1.3.1	Liquid Chlorine as specified in AWWA C652, (Ref. 1, Sec. 4.2.1)

7.1.3.2	Sodium Hypochlorite as specified in AWWA C652, (Ref. 1, Sec. 4.2.2)

7.1.3.3	Calcium Hypochlorite (HTH) is not acceptable.

NOTE: TBT recommends (Ref. 1, Sec. 4.2.2) Sodium Hypochlorite

7.1.4	Acceptable methods of chlorination per AWWA C652:

7.1.4.1	Ref. 1, Sec. 4.3.1-Chlorination Method 1

7.1.4.2	Ref. 1. Sec. 4.3.2 Chlorination Method 2 (chemical feed pump only (4.3.2.1))

7.1.4.3	Ref. 1, Sec. 4.3.3-Chlorination Method 3

NOTE: TBT recommends (Ref. 1, Sec. 4.3.3)-Chlorination Method 3

# PART 8 – TANK MANUFACTURER’S WARRANTY

8.1	The tank manufacturer shall include a warranty on tank materials and workmanship for a specified period. As a minimum, the warranty shall provide assurance against defects in material, coatings, and workmanship for a period of one (1) year.

8.2	Structure-The tank manufacturer shall warrant the liquid storage tank shall be free from any defect in material or workmanship, under normal and proper use, maintenance and operation, during the period expiring on the earlier of (i) 12 months after liquid is first introduced into the tank or (ii) 15 months after shipment from the factory.